| Canadian Natural Resources Limited GENERAL PRESSURE VESSEL INFORMATION Job# 05.003822 |
| --- |
| District: Fort St John, BC | Skid No. |
| Facility: Buick Creek South | Location (LSD): 09-34-88-20-W6M |
| Vessel Name Equipment Number: Produced Emulsion Tank 400 BBL |
| Orientation: Vertical |
| Status: In Service | Regulatory Inspection |
| PRESSURE VESSEL NAMEPLATE DATA |
| “A” or “G” or “S” (Sask.) or BC Registration Number. None | CRN Number: None |
| Vessel serial number: 15217 | Size: 12’ X 20’ |
| Shell thickness: 3/16” | Shell material: N/S |
| Bottom thickness: ¼” | Head material: N/S |
| Deck thickness: 3/16” | Tube material: |
| Tube diameter: | Tube length: |
| Channel thickness: | Channel material: |
| Design pressure | Shell: Atmos | Operating pressure | Shell: 0 PSI |
|  | Tubes: |  | Tubes: |
| Design Temp. | Shell: N/S | Operating temperature | Shell: No gauge |
|  | Tubes: |  | Tubes: |
| X-ray: N/S | Heat treatment: None |
| Code parameters: API 650 | Coated: No |
| Manufacturer: Argo Sales Ltd. | Year built: 1997 |
| Corrosion allowance: N/S | Manway: Yes |
| PRESSURE SAFETY VALVE NAMEPLATE DATA |
| PSV Tag # | Manufacture | Model # | Serial # | Set Pressure (PSI) | Capacity (scfm) | Service Date |
|  |  | Tank is Atmos |  |  |  |  |
| CRN # | Service By | Block Valve | Location | Size | Code Stamp |  |
| SERVICE CONDITIONS-INDICATE ALL THAT APPLY |
| Sweet | Sour X | Oil X | Gas | Water X |
| Amine | LPG | Condensate | Air | Glycol |
| Other (Describe): |

# Inspection Interval ________________________________________PSV Service Interval_________________________________

# (Determined by MIC in conjunction with Chief Inspector following guidelines of CNRL’s Owner-User Inspection Program)

Reports reviewed and accepted by:

# Mechanical Integrity Coordinator________________________________________________Date__________________________

# Fill out all forms as completely as possible. All information is important!  Use back of sheets to record additional information or sketch if required.

# Copy of report to be filed by MIC at site, and copy sent to Chief Inspector

| External Inspection Items | G | F | P | N/A | Comments |
| --- | --- | --- | --- | --- | --- |
| Insulation Verify sealed around manways, nozzles, no damage present, and there is no egress of moisture. |  |  |  | X | Tank is not insulated. |
| External Condition Assess paint condition, areas peeling, record any corrosion, damage, etc (record location, size and depth of corrosion or damage) |  | X |  |  | Paint is in fair overall condition – Exposed metal to approx 10% of the shell with surface corrosion. Minor dents noted on the upper shell sections. |
| Leakage Record any leakage at flanges, threaded joints, weep holes on repads, etc. | X |  |  |  | No leaking detected. |
| Saddle Assess condition of paint, fire protection, and concrete. Look for corrosion, buckling, dents, etc. Look at vessel surface area near supports. Verify no signs of leakage at attachment to vessel and attachment welds are acceptable. Ground wire attached? |  | X |  |  | No saddle. No corrosion – no missing paint. No ground cable attached to tank skid. |
| Anchor Bolts Hammer tap to ensure secure. Look for cracking in treads or signs of deformation. |  |  | X |  | Tank is set on top of pilings - tank is not secured either by bolting or welds. |
| Concrete foundation Check for cracks, spalling, etc. |  |  |  | X | None. |
| Ladder / Platform Describe general condition, ensure support is secure to vessel, and describe any hazards. | X |  |  |  | Ladder is firmly secured, no loose or missing bolts - paint is in good condition. |
| Nozzle Assess paint, look for leakage, and ensure stud threads are fully engaged. Record any damage, deflection, etc. Are nozzles gusseted? | X |  |  |  | All threads connections fully engaged. No deflection – no leaks. No gussets. |
| Gauges Ensure gauges are visible, working, no leakage, and suitable for range of MAWP/ Temp. | X |  |  |  | Level gauge is appears operational & legible. |
| External Piping Ensure pipe is well supported. All clamps, supports, shoes, etc. in place. Look for evidence of structural overload, deflection, etc. Paint condition, external corrosion? | X |  |  |  | Well supported – no deflection – all clamps and shoes in place. Piping is insulated and in good condition – visible damage found top flange is wrapped with temporary insulation wrap. |
| Valving Ensure no leaks are visible. Valves are properly supported and chained if necessary. | X |  |  |  | Well supported – no leaks. |
| PSV Ensure PSV is set at pressure at or below that of vessel. |  |  |  | X | Tank is atmospheric. |
| NDE methods Was UT/ MPI done on vessel (MI coordinator to review results) |  |  |  | X | None at this time. |
| Other Burm: | X |  |  |  | Tank is inside of a concrete burm - inspection limited due to snow coverage, no visible signs of leaks. |
| Recommendations or corrective actions : Vessel is Fit for Service or describe corrective actions required) (MIC to review corrective actions with Operations, discuss with Chief Inspector where necessary, and get remedial action implemented) Recommendations: 1. Secure the tank down by either welding or bolts. 2. Complete the insulation on the top inlet flange. 3. Install a ground cable. Summary: This tank is in good over all condition, visual external survey carried out. Tank is fit for service. |

Inspected By: Joe Holdstock								           Date: November-22-2009

| LSD location | Data plate |
| --- | --- |
| Overview | Surface corrosion & denting |
| Tank skid not secured | Burm overview |