| Canadian Natural Resources Limited GENERAL PRESSURE VESSEL INFORMATION |
| --- |
| District: Foxcreek Ab | Skid No. |
| Facility: Berland River Gas Plant | Location (LSD) 16-15-59-24 W5M |
| Vessel Name & Equipment Number: Inlet Separator |
| Orientation: Horizontal |
| Status: Operating | Precommissioning Inspection |
| PRESSURE VESSEL NAMEPLATE DATA |
| Registeration Number A 496381 | CRN Number R 1481.21 |
| Vessel serial number: PE 7964 | Size: 42 in. ID x 12 ft S/S |
| Shell thickness: 25.4 mm | Shell material: SA 516 70 |
| Head thickness: 25.4 mm | Head material: SA 516 70 |
| Tube wall thickness: | Tube material: |
| Tube diameter: | Tube length: |
| Channel thickness: | Channel material: |
| Design pressure | Shell: 825 psi | Operating pressure | Shell: |
|  | Tubes: |  | Tubes: |
| Design Temp. | Shell: 100 deg F | Operating temperature | Shell: |
|  | Tubes: |  | Tubes: |
| X-ray: RT 2 | Heat treatment: No |
| Code parameters: ASME VIII / Div 1 | Coated: No |
| Manufacturer: Penfabco Limited | Year built: 2003 |
| Corrosion allowance: 1.6 mm | Manway: Yes |
| PRESSURE SAFETY VALVE NAMEPLATE DATA |
| PSV Tag no. | Manufacture | Model | Serial number | Set Pressure | Capacity | Size |
| P 27120 | Crosby | JOS-E-45/J | CO5-04-239 | 800 psi | 12563 scfm | 2 in. x 3 in. |
| Serv By | Date | Block Valve | CRN number | Code Stamp | Location |  |
| Power Comm | Jul 03 | No | OG 0703.9C | UV | Top Shell |  |
| SERVICE CONDTIONS-INDICATE ALL THAT APPLY |
| Sweet X | Sour | Oil | Gas X | Water X |
| Amine | LPG | Condensate X | Air | Glycol |
| Other (Describe): |

81

# Inspection Interval ________________________________________PSV Service Interval_________________________________

# (Determined by MIC in conjunction with Chief Inspector following guidelines of  CNRL’s Owner-User Inspection Program)

Reports reviewed and accepted by:

# Mechanical Integrity Coordinator________________________________________________Date__________________________

# Fill out all forms as completely as possible. All information is important!  Use back of sheets to record additional information or sketch if required.

# Copy of report to be filed by MIC at site,  and copy sent to Chief Inspector

Inspected By:_______________________________________________________Date:____________________________________

### A # 496381													82

| External Inspection Items | G | F | P | N/A | Comments |
| --- | --- | --- | --- | --- | --- |
| Insulation Verify sealed around manways, nozzles, no damage present, and there is no egress of moisture. |  |  |  | X | Vessel is not insulated |
| External Condition Assess paint condition, areas peeling, record any corrosion, damage, etc (record location, size and depth of corrosion or damage) |  | X |  |  | No loose or flaking paint. |
| Leakage Record any leakage at flanges, threaded joints, weep holes on repads, etc. | X |  |  |  | No leaks detected. |
| Skirt Assess condition of paint, fire protection, concrete. Look for corrosion, buckling, dents, etc. Look at vessel surface area near supports. Verify no signs of leakage at attachment to vessel and attachment welds are acceptable. Ground wire attached? | X |  |  |  | Separator is mounted firmly to floor, no distortion to skirt. |
| Anchor Bolts Hammer tap to ensure secure. Look for cracking in treads or signs of deformation. | X |  |  |  | Firmly bolted. |
| Concrete foundation Check for cracks, spalling, etc. |  |  |  | X |  |
| Ladder / Platform Describe general condition, ensure support is secure to vessel, describe any hazards. |  |  |  | X |  |
| Nozzle Assess paint, look for leakage, and ensure stud threads are fully engaged. Record any damage, deflection, etc. Are nozzles gusseted? | X |  |  |  | Good condition, no leaking detected. |
| Gauges Ensure gauges are visible, working, no leakage, and suitable for range of MAWP/ Temp. | X |  |  |  | Firmly attached and within operational parameters for service. |
| External Piping Ensure pipe is well supported. All clamps, supports, shoes, etc. in place. Look for evidence of structural overload, deflection, etc. Paint condition, external corrosion? | X |  |  |  | Firmly supported, no distortion or deflection. |
| Valving Ensure no leaks are visible. Valves are properly supported and chained if necessary. | X |  |  |  | Firmly attached, no leaks. |
| PSV Ensure PSV is set at pressure at or below that of vessel. Discharge piping is same size as inlet to valve and is properly supported and routed. Ensure no block valves between psv and vessel or if there are they are locked open. |  |  |  |  | Located on inlet piping, set below MAWP of vessel. |
| NDE methods Was UT/ MPI done on vessel (MI coordinator to review results) | X |  |  |  | Corrosion survey carried out - Ultrasonic Test Point # 265 (3 inch drain elbow) has some general corrosion – UT min 6.4 mm. Code calculated to Minimum thickness 2.2 mm for operation. |
| Recommendations or corrective actions : Vessel is Fit for Service or describe corrective actions required) (MIC to review corrective actions with Operations, discuss with Chief Inspector where necessary, and get remedial action implemented) Monitor drain elbow – Point # 265 for corrosion progression. Vessel is fit for service. |

Inspected By:  D. Wiedman                                                                                                                                          Date: July 2003

3 Phase Inlet Separator – A 496381										83