| Record Motor Nameplate data : |
| --- |
| Manufacturer: TECO | Serial Number: LX912B036002 |
| Model Number: | Type : AEHH8B-UWX | Duty: CONTINUOUS |
| HP / kW : (Circle) 75HP | Volts: 575 VOLTS | Full Load Current: 76.5 AMPS |
| RPM: 885 RPM | Frame: 444T | Insulation Class: F |
| Temperature Rise: XXXX | Amb.Temp: 40 C | Service Factor: 1.15 |
| Hz: 60 HZ | CAT# APH07585-841 |
| Anti-Condensation Heater |
| No. | Items to be checked: Refer 00-FM-EL-0046 | Complete Yes | Complete No | N/A |
| DB | Verify motor enclosure type is suitable for use in area classification. | YES |  |  |
| DB | Verify the motor has been insulation resistance tested | YES |  |  |
| DB | Verify motor power cable, control wires and associated devices tagging is the same as per drawing | YES |  |  |
| DB | Verify the grounding and bonding conductors are installed/connected | YES |  |  |
| DB | Verify motor power cables are properly terminated and check that conductors are installed in motor junction box without excessive stress. | YES |  |  |
| DB | Motor electrical accessories (e.g. space heaters, thermistors, RTDs and vibration switches) are properly connected, functioning and communicating both locally and in the DCS. | YES |  |  |

| DB | Covers are installed, bolt and nuts tightened to spec torque. | YES |  |  |
| --- | --- | --- | --- | --- |
| DB | Verify relay program and communication to DCS as per engineering document | YES |  |  |
| DB | Function test of the local control station (LCS) as per drawing and verify status in DCS | YES |  |  |
| DB | Verify proper lubrication of the motor bearing as per vender recommendation. | YES |  |  |
|  | If motor is driven by VFD, complete checklist for VFD |  |  |  |
| DB | Verify actual Speed and FLA on local panel asper engineering specification and compare reading with DCS in MCR | YES |  |  |
|  | Verify that the rotation is checked. Baseline vibration and current are checked during solo-run. Standing from NDE is the motor turning CW or CCW select one. | CW/CCW |  |  |
|  | Final inspection completed. Deficiency list items cleared. |  |  |  |
| Remarks: Speed and Current reading are in Percentage in DCS . For items that have readings or specifications please record. |