| Canadian Natural Resources Limited GENERAL PRESSURE VESSEL INFORMATION Job # 05.01510 |
| --- |
| District: Fort St John, B.C. | Skid No. |
| Facility: North Nig Compressor Station | Location (LSD): d-41-J/94-H-4 |
| Vessel Name Equipment Number: 3 Phase Separator |
| Orientation: Vertical |
| Status: In Service | Regulatory Inspection |
| PRESSURE VESSEL NAMEPLATE DATA |
| “A” or “G” or “S” (Sask.) or BC Registration Number. A3105881 | CRN Number: H-2451.2 |
| Vessel serial number: 3525 | Size: 16 in x 90 in |
| Shell thickness: 26.2 mm | Shell material: SA 106 B |
| Head thickness: 23.8 mm | Head material: SA 516-70 |
| Tube wall thickness: | Tube material: |
| Tube diameter: | Tube length: |
| Channel thickness: | Channel material: |
| Design pressure | Shell: 9928 kPa | Operation pressure | Shell: |
|  | Tubes: |  | Tubes: |
| Design Temp. | Shell: 38°C | Operation Temp. | Shell: |
|  | Tubes: |  | Tubes: |
| X-ray: RT-2 | Heat treatment: HT |
| Code parameters: ASME VIII, Div 1 | Coated: No |
| Manufacturer: RJV Gas Field Services LTD. | Year built: 1995 |
| Corrosion allowance: 3.2 mm | Manway: No |
| PRESSURE SAFETY VALVE NAMEPLATE DATA |
| PSV Tag # | Manufacture | Model # | Serial # | Set Pressure (kPa) | Capacity (scfm) | Service Date |
| 4641F | Taylor | 82E7351311 | 69875-26 | 9928 | 5181 | 04/2009 |
| CRN # | Service By | Block Valve | Location | Size | Code Stamp |  |
| OG1316.2341YT | Unified Valve | No | Mid Shell | 1” x 1” | UV/NB |  |
| SERVICE CONDITIONS-INDICATE ALL THAT APPLY |
| Sweet X | Sour | Oil | Gas X | Water X |
| Amine | LPG | Condensate X | Air | Glycol |
| Other (Describe): |

# Inspection Interval ________________________________________PSV Service Interval_________________________________

# (Determined by MIC in conjunction with Chief Inspector following guidelines of CNRL’s Owner-User Inspection Program)

Reports reviewed and accepted by:

# Mechanical Integrity Coordinator________________________________________________Date__________________________

# Fill out all forms as completely as possible. All information is important!  Use back of sheets to record additional information or sketch if required.

# Copy of report to be filed by MIC at site, and copy sent to Chief Inspector

# A3105881

| External Inspection Items | G | F | P | N/A | Comments |
| --- | --- | --- | --- | --- | --- |
| Insulation Verify sealed around manways, nozzles, no damage present, and there is no egress of moisture. |  |  |  | X | No insulation. Roof seal intact. |
| External Condition Assess paint condition, areas peeling, record any corrosion, damage, etc (record location, size and depth of corrosion or damage) | X |  |  |  | Paint failed in areas to 5% with corrosion occurring |
| Leakage Record any leakage at flanges, threaded joints, weep holes on repads, etc. | X |  |  |  | No leaking detected. |
| Saddle/skirt Assess condition of paint, fire protection, and concrete. Look for corrosion, buckling, dents, etc. Look at vessel surface area near supports. Verify no signs of leakage at attachment to vessel and attachment welds are acceptable. Ground wire attached? | X |  |  |  | Skirt is in good condition – no buckles or distortion. Paint intact – with little to no corrosion. Vessel grounded through the skid package. No signs of leakage. |
| Anchor Bolts Hammer tap to ensure secure. Look for cracking in treads or signs of deformation. | X |  |  |  | Firmly secured. Welded to Skid No signs of deformation. |
| Concrete foundation Check for cracks, spalling, etc. |  |  |  | X | None. |
| Ladder / Platform Describe general condition, ensure support is secure to vessel, and describe any hazards. |  |  |  | X | None. |
| Nozzle Assess paint, look for leakage, and ensure stud threads are fully engaged. Record any damage, deflection, etc. Are nozzles gusseted? | X |  |  |  | All threads engaged. No deflection – no leaks. Stud threads fully engaged, no gussets. Painting good overall condition. |
| Gauges Ensure gauges are visible, working, no leakage, and suitable for range of MAWP/ Temp. | X |  |  |  | Pressure Gauge (0-1500 PSI) Suitable for MAWP Clear and clean. |
| External Piping Ensure pipe is well supported. All clamps, supports, shoes, etc. in place. Look for evidence of structural overload, deflection, etc. Paint condition, external corrosion? | X |  |  |  | Well supported – no deflection – all clamps and shoes in place. Piping is painted and is in good overall condition. |
| Valving Ensure no leaks are visible. Valves are properly supported and chained if necessary. | X |  |  |  | Well supported – no leaks. |
| PSV Ensure PSV is set at pressure at or below that of vessel. Discharge piping is same size as inlet to valve and is properly supported and routed. Ensure no block valves between PSV and vessel or if there are they are locked open. | X |  |  |  | PSV is set below MAWP of vessel. PSV Discharge piping is larger than inlet piping and is properly supported and routed. Car Seals Intact. Location: Mid Shell |
| NDE methods Was UT/ MPI done on vessel (MI coordinator to review results) | X |  |  |  | Ultrasonic corrosion survey carried out – head and shell metal thickness detected below nominal minus corrosion allowance. Thickness calculations carried out: UT point 715 (Mid Shell) – nominal thickness is 26.2mm / min thickness is 26.0mm / T min thickness is 18.4mm. UT point 725 (Bottom Head) – nominal thickness is 23.8mm / min thickness is 23.4mm / T min thickness is 15.1mm. |
| Recommendations or corrective actions : Vessel is Fit for Service or describe corrective actions required) (MIC to review corrective actions with Operations, discuss with Chief Inspector where necessary, and get remedial action implemented) Recommendations: No recommendations at this time. Summary: This vessel is in good overall condition, Ultrasonic thickness survey carried out - no metal thickness detected below nominal minus corrosion allowance. Long term corrosion rate based on greatest thickness loss (Head) 0.025mm per year. Retirement Date to “T”min is year 2343. Vessel is fit for service. |

Inspected By: Dellas Weidman				                                                                               Date: Feb 03, 2011

|  | Data Plate Overview |
| --- | --- |
| Pressure Gauge | Overview |
| Skirt | PSV Tag |
| PSV Tag | PSV Tag |