## Shutdown Key
[7 empty] | Column # | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
[8 empty] | 1: IGNITION MODULE 1 (IGN1) Enabled; 5: IGNITION MODULE 2 (IGN2) Enabled | IGNITION MODULE 1 (IGN1) Enabled |  |  |  | IGNITION MODULE 2 (IGN2) Enabled
[8 empty] | 1: Intermittent Mode; 5: Intermittent Mode | Continuous Mode |  |  |  | Continuous Mode
|  |  | Legend |  |  |  |  | 1: TC1 < IGN1 TC1 Setpoint Temp; 5: TC1 < IGN2 TC1 Setpoint Temp | TC1 < IGN1 TC1 Setpoint Temp |  |  |  | TC1 < IGN2 TC1 Setpoint Temp
|  |  | SD | ACL-1500 Shutdown |  |  | Output Description | IGN1 Burner Permissive (and if enabled) | IGN1 Pilot Solenoid Valve Output | IGN1 Main Solenoid Valve Output | IGN1 Temperature Main (T/Main) Solenoid Valve Output | IGN2 Burner Permissive (and if enabled) | IGN2 Pilot Solenoid Valve Output | IGN2 Main Solenoid Valve Output | IGN2 Temperature Main (T/Main) Solenoid Valve Output | IGN1 Burner Permissive (and if enabled) | IGN1 Pilot Solenoid Valve Output | IGN1 Main Solenoid Valve Output | IGN1 Temperature Main (T/Main) Solenoid Valve Output | IGN2 Burner Permissive (and if enabled) | IGN2 Pilot Solenoid Valve Output | IGN2 Main Solenoid Valve Output | IGN2 Temperature Main (T/Main) Solenoid Valve Output | 4-20mA Output 1, Proportional Valve (PVLV) mode | 4-20mA Output 2, Proportional Valve (PVLV) mode | AUX1 Relay | AUX2 Relay
|  |  | CL | Closed Valve
|  |  | OP | Opened Valve
|  |  | 4 | 4mA on 4-20mA Output (closed temp control valve)
|  |  | AO | Alarm Only, no Shutdown
|  |  | P | Permissive
|  |  | N/A | Not applicable / No component to control
|  |  | ATOP | Allowed To Open
Row # | ALARM/Status Contacts (32, 33, 34): Short = NC-COM or NO-COM | Shutdown Code on Display | Function Tested | Shutdown / Input | Configuration | Conditions | Terminal # |  | 67 & 68 | 65 & 66 | 63 & 64 |  | 56 & 57 | 54 & 55 | 52 & 53 |  | 67 & 68 | 65 & 66 | 63 & 64 |  | 56 & 57 | 54 & 55 | 52 & 53 | 14 & 15 | 16 & 17 | 39 - 41 | 42 - 44
Normal Shutdowns:
1 | NC-COM |  | Yes | Power Off (Manual ESD) |  |  | N/A | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | 0 | 0 | NC-COM | NC-COM
2 | NC-COM | "OFF" | Yes | Stop Button |  |  | N/A | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | 4 | 4 | NC-COM | NC-COM
3 | NC-COM | "POC" | Yes | Proof of Closure Terminals |  | Open Upon Start | 18 & 19 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | 4 | 4
4 | NC-COM |  | Yes | Proof of Closure Terminals |  | Closed Upon Start | 18 & 19 | P ACL-1500 | ATOP XV-4452 XV-4453 | N/A | ATOP XV-4450 | P ACL-1500 | ATOP XV-4452 XV-4453 | N/A | ATOP XV-4450 | P ACL-1500 | ATOP XV-4452 XV-4453 | N/A | ATOP XV-4450 | P ACL-1500 | ATOP XV-4452 XV-4453 | N/A | ATOP XV-4450
5 | NC-COM | "REM STOP" | Yes | Remote Start/Stop Terminals |  |  | 20 & 21 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | 4 | 4
6 | NC-COM | "HIGH GAS" | Yes | High Gas Pressure Shutdown Terminals |  |  | 22 & 23 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | 4 | 4 | NC-COM | NC-COM
7 | NC-COM | "LOW GAS" | Yes | Low Gas Pressure Shutdown Terminals |  |  | 24 & 25 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | 4 | 4 | NC-COM | NC-COM
8 | NC-COM | "LEVEL" | Yes | Level Shutdown Terminals |  |  | 26 & 27 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | 4 | 4 | NC-COM | NC-COM
9 | NC-COM | "AUX 1" | Yes | Auxiliary 1 Shutdown Terminals |  |  | 28 & 29 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | 4 | 4 | NC-COM | NC-COM
10 | NC-COM | "AUX 2" | Yes | Auxiliary 2 Shutdown Terminals |  |  | 30 & 31 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | 4 | 4 | NC-COM | NC-COM
11 | NC-COM | "HI TEMP" | Yes | TC2 High Temperature SD |  |  | TC2 (6 & 7) | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | 4 | 4 | NC-COM | NC-COM
12 | NC-COM | "HT TC3" | Yes | TC3 Auxiliary High Temp SD (if enabled) |  |  | TC3 (8 & 9) | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | 4 | 4 | NC-COM | NC-COM
4-20mA Input Alarm/Shutdowns:
|  |  |  | 4-20mA Input 1 - 12/24VDC Power output |  |  | 10
13 |  | "420 1* LO" | Yes | 4-20mA Input 1 - 4-20mA Input signal | Lo Alarm Enabled, SD on Low Alarm Disabled | Input < Lo TripPt | 11 | AO ACL-1500 | OP XV-4452 XV-4453 | N/A | OP XV-4450 | AO ACL-1500 | OP XV-4452 XV-4453 | N/A | OP XV-4450 | AO ACL-1500 | OP XV-4452 XV-4453 | N/A | OP XV-4450 | AO ACL-1500 | OP XV-4452 XV-4453 | N/A | OP XV-4450 |  |  | * No Change | * No Change
14 |  | "420 1 LO" | Yes | 4-20mA Input 1 - 4-20mA Input signal | Lo Alarm Enabled, SD on Low Alarm Enabled | Input < Lo TripPt | 11 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | 4 | 4 | NC-COM | NC-COM
15 |  | "420 1* HI" | Yes | 4-20mA Input 1 - 4-20mA Input signal | Hi Alarm Enabled, SD on Hi Alarm Disabled | Input > Hi TripPt | 11 | AO ACL-1500 | OP XV-4452 XV-4453 | N/A | OP XV-4450 | AO ACL-1500 | OP XV-4452 XV-4453 | N/A | OP XV-4450 | AO ACL-1500 | OP XV-4452 XV-4453 | N/A | OP XV-4450 | AO ACL-1500 | OP XV-4452 XV-4453 | N/A | OP XV-4450 |  |  | * No Change | * No Change
16 |  | "420 1 HI" | Yes | 4-20mA Input 1 - 4-20mA Input signal | Hi Alarm Enabled, SD on Hi Alarm Enabled | Input > Hi TripPt | 11 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | 4 | 4 | NC-COM | NC-COM
|  |  |  | 4-20mA Input 2 - 12/24VDC Power output |  |  | 12
17 |  | "420 2* LO" | Yes | 4-20mA Input 2 - 4-20mA Input signal | Lo Alarm Enabled, SD on Low Alarm Disabled | Input < Lo TripPt | 13 | AO ACL-1500 | OP XV-4452 XV-4453 | N/A | OP XV-4450 | AO ACL-1500 | OP XV-4452 XV-4453 | N/A | OP XV-4450 | AO ACL-1500 | OP XV-4452 XV-4453 | N/A | OP XV-4450 | AO ACL-1500 | OP XV-4452 XV-4453 | N/A | OP XV-4450 |  |  | * No Change | * No Change
18 |  | "420 2 LO" | Yes | 4-20mA Input 2 - 4-20mA Input signal | Lo Alarm Enabled, SD on Low Alarm Enabled | Input < Lo TripPt | 13 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | 4 | 4 | NC-COM | NC-COM
19 |  | "420 2* HI" | Yes | 4-20mA Input 2 - 4-20mA Input signal | Hi Alarm Enabled, SD on Hi Alarm Disabled | Input > Hi TripPt | 13 | AO ACL-1500 | OP XV-4452 XV-4453 | N/A | OP XV-4450 | AO ACL-1500 | OP XV-4452 XV-4453 | N/A | OP XV-4450 | AO ACL-1500 | OP XV-4452 XV-4453 | N/A | OP XV-4450 | AO ACL-1500 | OP XV-4452 XV-4453 | N/A | OP XV-4450 |  |  | * No Change | * No Change
20 |  | "420 2 HI" | Yes | 4-20mA Input 2 - 4-20mA Input signal | Hi Alarm Enabled, SD on Hi Alarm Enabled | Input > Hi TripPt | 13 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | SD ACL-1500 | CL XV-4452 XV-4453 | N/A | CL XV-4450 | 4 | 4 | NC-COM | NC-COM
"* No Change" - depends on selected mode for AUX relay